ORDINANCE NO.  5 - 2010

AN ORDINANCE AMENDING THE

CENTRAL STICKNEY FIRE PROTECTION DISTRICT

FIRE CODE TO ADOPT THE 2009 INTERNATIONAL FIRE CODE WITH

# AMENDMENTS AS THE FIRE CODE OF THE

# CENTRAL STICKNEY FIRE PROTECTION DISTRICT

WHEREAS, code officials have long recognized the need for a single, up-to-date Fire Code applicable throughout the country; and

WHEREAS, representatives of the three major code writing organizations, Building Officials and Code Administrations International, Inc. (BOCA), International Conference of Building Officials (ICBO), and Southern Building Code Congress International, Inc. (SBCCI), have joined together to develop one International Fire Code (IFC), for the entire country; and

WHEREAS, the Board of Trustees of the District deems it in the best interests of the District to adopt the 2009 International Fire Code with certain deletions and amendments; and

WHEREAS, a copy of the 2009 International Fire Code has been on file with the District for thirty (30) days and has, during that time, been available for public use, inspection, and examination.

NOW, THEREFORE, Be it ordained by the President and Board of Trustees of the Central Stickney Fire Protection District, Cook Counties, Illinois, as follows:

SECTION 1

The Central Stickney Fire Protection District Fire Code is hereby amended to delete and repeal the present language in its entirety and substitute the following:

1-1-1:  IFC 2009 ADOPTED:

Adopted and applicable as the Fire Code of the Central Stickney Fire Protection District are those rules and regulations set forth with particularity in the booklet entitled “International Fire Code 2009”, published by the International Code Council, Inc., amended, however, in that the following portions indicated in Section 1-1-2 hereof are not hereby adopted, or are hereby amended or added to that Code as indicated in Section 1-1-3 and as set forth with particularity in the document entitled “International Fire Code 2009.”

SECTION 2

The Fire Code of the Central Stickney Fire Protection District is hereby amended to delete in their entirety the following sections and subsections of the International Fire Code 2009.

    - DELETIONS FROM IFC 2009:

- 101.1		Title

- 102.3		Change of Use or Occupancy

- 105.3.6		Compliance With Code

- 105.4.4		Approved Documents

- 108.1		Board of Appeals Established

- 109.3		Violation Penalties

- 111.4		Failure to Comply

- 202		Definitions:

-  Change of Occupancy

-  Fire Watch

- 307.4.1		Bonfires

- 307.4.2		Recreational Fires

- 308.3.1.1		Liquefied Petroleum Gas-Fueled Devices

- 309.4		Fire Extinguishers

- 311.2.2		Fire Protection

- 404.2		Where Required

- 503.1		Where Required

- Exception 1 to 503.1.1

- 503.2.1		Dimensions

- 503.2.4		Turning Radius

- 503.2.5		Dead Ends

- 505.1		Address Numbers

- 506.1		When Required

- 806.1.1		Restricted Occupancies

- Exceptions 1 and 2 to 807.4.3.1

- Exceptions 1 and 2 to 807.4.4.1

- 903.2.1.1		Group A-1

- 903.2.1.2		Group A-2

- 903.2.1.3		Group A-3

- 903.2.1.4		Group A-4

- 903.2.1.5		Group A-5

- 903.2.3		Group E

- 903.2.4		Group F-1

- 903.2.5		Group H

- 903.2.5.1		General

- 903.2.5.2		Group H-5 Occupancies

- Table 903.2.5.2

- 903.2.5.3		Pyroxylin Plastics

- 903.2.6		Group I

- 903.2.7		Group M

- 903.2.7.1		High-Piled Storage

- 903.2.8		Group R

- 903.2.9		Group S-1

- 903.2.9.1		Repair Garages

- 903.2.9.2		Bulk Storage of Tires

- 903.2.10		Group S-2

- 903.2.10.1		Commercial Parking Garages

- Exception to 903.2.11

- 903.2.11.1		Stories and Basements Without Openings

- 903.2.11.1.2	Openings on One Side Only

- 903.2.11.1.3	Basements

- 903.3.1		Standards

- 903.3.1.1.1		Exempt Locations

- 903.3.1.2		NFPA 13R Sprinkler Systems

- 903.3.1.3		NFPA 13D Sprinkler Systems

- 903.3.5		Water Supplies

- 903.3.5.1		Water Supply

- 903.3.7		Fire Department Comments

- Exceptions 2, 4 and 5 to 903.4

- 903.4.1	Signals

- 904.3.5	Monitoring

- 905.3.1	Height

- Exception to 906.1(1)

- 906.3		Size and Distribution

- 907.2		Where Required-New Buildings and Structures

- 907.2.1	Group A

- 907.2.2	Group B

- 907.2.3	Group E

- 907.2.4	Group F

- 907.2.5	Group H

- 907.2.6	Group I

- Exception 1 to 907.2.6.1

- 907.2.6.2	Group I-2

- 907.2.6.3	Group I-3 Occupancies

- 907.2.7	Group M

- 907.2.8	Group R-1

- 907.2.9	Group R-2

- 907.2.10	Group R-4

- 907.2.11.2   	Group I-1

- 907.2.13	High-Rise Buildings

- 907.7.2	Power Supply

- 907.7.3	Zones

- 907.4.1	Duct Smoke Detectors

- 908.1		Group H Occupancies

- 912.2		Location

- 912.5		Backflow Protection

- 913.4		Valve Supervision

- Exception to 914.2.1(2)

- Exceptions to 914.3.1

- Exceptions to 914.4.1

- Exceptions to 914.7.1

- 1003.1		Applicability

- Exceptions to 1006.1

- Exceptions to 1006.2

- 1006.3		Illumination Emergency Power

- Exceptions to 1007.2.1

- Exceptions to 1007.3

- 1008.1.9.3	Locks and Latches

- Exceptions  to 1011.1

- 1011.2		Illumination

- Exception 6 to 1013.1

- 1417.3		Fire Extinguishers for Roofing Operations

- Exceptions to 1504.2

- 2404.12		Portable Fire Extinguishers

- 2701.3.3.1	Properties of Hazardous Materials

- Exceptions 2 and 4 to 3301.1.3

- 3302		Definitions

-Fireworks, 1.4G

- 3308.1		General

- 3308.2.1	outdoor Display

- 3309.1		General

- Appendix A

- Appendix B

- Appendix C

- Appendix E

- Appendix F

- Appendix G

SECTION 3

The Fire Code of the Central Stickney Fire Protection District is hereby amended to include in their entirety the following sections and subsections as set forth in the International Fire Code 2009:

1-1-3:  AMENDMENTS TO IFC 2009 AS SET FORTH IN IFC 2009:

- 101.1		Title

- 101.2.2		Name Change

- 101.5.1		Conflicting Code Information

- 101.6		NFPA Appendixes

- 102.3		Change of Use or Occupancy

- 104.6.5		Written Request for Records

- 105.3.6		Compliance With Code

- 105.3.6.1		Compliance

- 105.3.9		Certificate of Occupancy

- 105.4.4		Approved Documents

- 106.5		Inspection and Enforcement process

- 108.1		Board of Appeals Established

- 109.3		Violation Penalties

- 110.5		Fire Watch

- 111.4		Failure to Comply

- 202		Definitions:

-  Board of Trustees

-  Building

-  Building Code

-  Certificate of Use and Occupancy

-  Change of Occupancy

-  Change of Use

-  Code Official

-  Fire Watch

- 307.4.1		Bonfires

- 307.4.2		Recreational Fires

- 308.3.1.1		Liquefied Petroleum Gas-Fueled Devices

- 309.4		Fire Extinguishers

- 311.2.2  		Fire Protection

- 311.2.4		Fire Protection Up Grades

- 312.4		Gas Meter Protection

- 404.2		Where Required

- 503.1		Where Required

- 503.1.1.1		Public/Private Access for Fire Apparatus

- 503.2.1		Dimensions

- 503.2.4		Turning Radius

- 503.2.5		Dead Ends

- 503.3.1		Fire Lanes

- 505.1		Address Numbers

- 506.1		When Required

- 506.1.2		Type of Key Box

- 506.1.3		Location and Number:  Knox Box Location

- 506.1.4		Outside Strobe

- 506.3		Electric Shunt Switch

- 507.2.3		Fire Hydrant Water Supply

- 507.5.1		Where Required

- 507.5.1.1		Fire Department Connections

- 507.5.7		Fire Hydrant Installation

- 508.1.6		Fire Command Center

- 509.2		Access to Fire Equipment

- 511.1		Emergency Notification

- 607.1.1		Automatic Elevators for Fire Department Use

- 607.5		Elevator Phone

- 609.4		Hood System Suppression

- 806.1.1		Restricted Occupancies

- 901.2.2		Fire Alarm Installers

- 901.9.1		Materials and Contents Information

- 902.1		Definitions

-  Total Area

- 903.2.1.1		Group A-1

- 903.2.1.2		Group A-2

- 903.2.1.3		Group A-3

- 903.2.1.4		Group A-4

- 903.2.1.5		Group A-5

- 903.2.1.6		All Group A Occupancies

- 903.2.2		Group B

- 903.2.3		Group E

- 903.2.4		Group F-1

- 903.2.5		Group H

- 903.2.6		Group I

- 903.2.7		Group M

- 903.2.8		Group R

- 903.2.9		Group S-1

- 903.2.9.1		Repair Garages

- 903.2.9.2		Bulk Storage of Tires

- 903.2.10		Group S-2

- 903.2.10.1		Commercial Parking Garages

- 903.2.11.1		Stories and Basements Without Openings

- 903.2.11.1.2	Openings on One Side Only

- 903.2.11.1.3	Basements

- 903.3.1		Standards

- 903.3.1.2		NFPA 13R Sprinkler Systems

- 903.3.1.3		NFPA 13D Sprinkler Systems

- 903.3.5		Water Supplies

- 903.3.5.1		Water Supply

- 903.3.5.3	Safety Factor

- 903.3.5.4	Multi Tenant Occupancy

- 903.3.7	Fire Department Connections

- 903.4.1	Signals

- 903.4.2.1	Sprinkler Alarms

- 903.4.3.1	Multiple Story Buildings

- 903.4.3.2	Floor Plan

- 903.4.4	Hydraulic Calculations

- 903.4.5	Fire Pumps

- 903.5.1	Inspectors Test Valves

- 904.3.5	Monitoring

- 905.2.1	Standpipe System Design

- 905.3.1	Height

- 905.3.1.1	Building Area

- 905.3.1.2	System Required

- 905.3.1.3	High Rise Buildings

- 905.3.1.4	Open Parking Structures

- 905.12		Pressure-regulating Devices

- 906.3		Size and Distribution

- 906.4.1	Wet Chemical Based Fire Extinguishers

- 906.5.1	Within 5 Feet of Exit Door

- 907.1.4	Underwriters Laboratory Certificates

- 907.1.5	UL Certificates Existing Systems

- 907.1.6	UL Fire Alarm Installation Requirements

- 907.1.7	Where Required-Existing Buildings and Structures

- 907.2		Where Required-New Buildings and Structures

- 907.2.1  	Group A

- 907.2.2  	Group B

- 907.2.3 	Group E

- 907.2.4  	Group F

- 907.2.5	Group H

- 907.2.6  	Group I

- 907.2.6.2  	Group I-2

- 907.2.6.3	Group I-3 Occupancies

- 907.2.7 	Group M

- 907.2.8	Group R-1

- 907.2.9  	Group R-2

- 907.2.10	Group R-4

- 907.2.10.1.1	Additional Detection

- 907.2.11.2	Group I-1

- 907.2.11.2.1    Group S

- 907.2.13 	High-Rise Buildings

- 907.7.2	Power Supply

- 907.7.3	Zones

- 907.4.1	Duct Smoke Detectors

- 907.4.3.1	Elevator Emergency Telephones

- 907.9.6	Records of Completion

- 908.1		Group H Occupancies

- 909.20.6

- 909.20.6.1

- 912.1.1	Stotz Connection

- 912.2		Location

- 912.5		Backflow Protection

- 913.4		Valve Supervision

- 1003.1		Applicability

- 1006.3		Illumination Emergency Power

- 1008.1.8.3	Locks and Latches

- 1011.1.2	Floor Proximity Exit Signs

- 1011.1.3	Floor Proximity Egress Path Marking

- 1011.2		Illumination

- 1405.7		Barrier Protection/Containment

- 1417.3		Fire Extinguishers for Roofing Operations

- 2404.12	Portable Fire Extinguishers

- 2404.14.1	Occupant Load Sign

- 2701.3.3.1	Properties of Hazardous Materials

- Exception 5 to 3301.1.3

- 3302		Definitions

-Fireworks, 1.4G

- 3308.1		General

- 3308.1.1	General requirements for all Pyrotechnic/Consumer Fireworks Display

- 3308.2.1	Outdoor Display

- 3308.2.3	Permit Fee

- 3308.3.1	Pyrotechnic Operator and Licensing Rules

- 3308.8.1	Fire Department Supervision of Displays

- 3308.11	Retail Display and Sale

- 3308.12	Consumer Fireworks

- Appendix A	Basic Fire Control Measures

- Appendix B	Fire Alarm Plan Submittal Checklist

- Appendix C	Sprinkler System Plan Submittal Checklist

- Appendix E	Written Request for Records

- Attachment A	Referenced Codes and Standards

- Attachment B	Fees

SECTION 4  		PENALTIES – FIRE PREVENTION CODE

Any person who shall violate any of the provisions of this Ordinance or the Codes hereby adopted or fail to comply therewith, or who shall violate or fail to comply with any order made thereunder, or fail to pay a fee or fine set by this Ordinance or the Codes hereby adopted, or who shall build in violation of any detailed statement of specifications or plans submitted and approved thereunder and from which no appeal has been taken, or who shall fail to comply with such an order as affirmed or modified by the Board of Trustees or the Code Official or by a court of competent jurisdiction, within the time fixed therein, shall severally for each and every such violation and noncompliance respectively, be punishable by a fine of not less than Fifty ($50.00) Dollars nor more than One Thousand ($1,000.00) Dollars, plus all legal fees and all costs caused by enforcement.  Any such violation shall also be required to be corrected or remedied by all such persons as soon as possible.  Each day that prohibited conditions are maintained shall constitute a separate offense.

The application of the above penalty shall not be held to prevent the enforced removal of prohibited conditions, including the issuance of mandatory injunctions.

# SECTION 5   	SAVINGS CLAUSE

That nothing in this Ordinance or in the Building and Fire Prevention Codes hereby adopted shall be construed to affect any lawsuit or proceeding pending in any court, or any rights acquired, or liability incurred, or any cause or causes of action acquired or existing, under any act or ordinance hereby repealed as cited in Section 2 of this Ordinance; nor shall any just or legal right or remedy of any character be lost, impaired or affected by this Ordinance.

# SECTION 6	SEVERABILITY

6.1 It is hereby declared to be the intention of the Board of Trustees of the Central Stickney Fire Protection District that the several provisions of this Ordinance, and all codes adopted hereby, are severable, in accordance with the following:

- If any Court of competent jurisdiction shall adjudge any section, subsection, paragraph, sentence, clause, phrase or word of this Ordinance or the Codes adopted hereby to be invalid, such judgment shall not affect any other section, subsection, paragraph, sentence, clause, phrase or word of this Ordinance, or the Codes adopted hereby, not specifically included in said judgment, and

- If any court of competent jurisdiction shall invalidate the application of any section, subsection, paragraph, sentence, clause, phrase or word of this Ordinance or Codes adopted hereby to a particular property, building, or other structure, or any items of personal property, such judgment shall not affect the clause, phrase or word of this Ordinance or Codes adopted hereby to any property, building, structure, or personal property not specifically included in said judgment.

6.2  It is the declaration of the Board of Trustees of the Central Stickney Fire Protection District that if any section, subsection, paragraph, sentence, clause, phrase or word of this Ordinance or Codes adopted hereby be adjudged by a court of competent jurisdiction to be invalid, all remaining sections, subsections, paragraphs, sentences, clauses, phrases and words of this Ordinance, or Codes adopted hereby, would have been enacted by the Board of Trustees without the incorporation in this Ordinance, or Codes adopted hereby, of any such invalid or unconstitutional section, subsection, paragraph, sentence, clause, phrase or word of this Ordinance, or Codes adopted hereby.

# SECTION 7	 	EFFECTIVE DATE

That the provisions of this Ordinance shall be in full force and effect from and after its passage, and approval, and ten (10) days after publication as provided by law.  Copies of the International Fire Code 2009, Exhibit A and any section, additions or revisions shall be available for public inspection at the Administration Office, 4951 S. Louts Ave., Stickney Twp, Illinois, during normal business hours.

ADOPTED this 8th day of April, 2010, by a roll call vote as follows:

AYES:      ___(3)______________________________________________

NAYS:      ___(0)______________________________________________

ABSENT:  ___(0)______________________________________________

_________________________

President, Board of Trustees

Central Stickney Fire Protection District

ATTEST:

________________________

Secretary, Board of Trustees

Central Stickney Fire Protection District

(CORPORATE SEAL AFFIXED)

INTERNATIONAL

FIRE CODE

2009

TABLE OF CONTENTS

SECTION 101	  ADMINISTRATION - GENERAL……………………………………	Page   1

SECTION 102	  APPLICABILITY……………………………………………………...	Page   1

SECTION 104       GENERAL AUTHORITY AND RESPONSIBILITIES……………....	Page   1

SECTION 105       PERMIT………………………………………………………………..Page   1

SECTION 106       INSPECTIONS………………………………...……………………....Page   2

SECTION 108	  BOARD OF APPEALS………………………………………………..	Page   2

SECTION 109      VIOLATIONS…………………………………………………………	Page   2

SECTION 110	  UNSAFE BUILDINGS………………………………………………..	Page   3

SECTION 111	  STOP WORK ORDER………………………………………...............	Page   3

SECTION 202       GENERAL DEFINITIONS……………………………………………Page   3

SECTION 307       OPEN BURNING AND RECREATIONAL FIRES ………………….	Page   4

SECTION 308       OPEN FLAMES ………………………………………………………	Page   4

SECTION 309       POWERED INDUSTRIAL TRUCKS AND EQUIPMENT…………..	Page   4

SECTION 311	  VACANT PREMISES…………………………………………………	Page   4

SECTION 312	  VEHICLE IMPACT PROTECTION……………………………….….Page   5

SECTION 404	  FIRE SAFETY AND EVACUATION PLANS……………………….	Page   5

SECTION 503       FIRE APPARATUS ACCESS ROADS………………………………	Page   5

SECTION 505	  PREMISES IDENTIFICATION…………………………………... ….Page   5

SECTION 506	  KEY BOXES…………………………………………………………..	Page   6

SECTION 507       FIRE PROTECTION WATER SUPPLIES …………….…………….	Page   6

SECTION 508       FIRE COMMAND CENTER…………….…………………………....	Page   7

SECTION 509	  FIRE DEPARTMENT ACCESS TO EQUIPMENT………………….	Page   7

SECTION 511       EMERGENCY NOTIFICATION……………………………………..	Page   7

SECTION 607	  ELEVATOR RECALL AND MAINTENANCE……………...............	Page   7

SECTION 609       COMMERCIAL KITCHEN HOODS…………………………………	Page   8

SECTION 806       DECORATIVE VEGETATION IN NEW AND

EXISTING BUILDINGS……………………………….……..Page   8

SECTION 807       DECORATIVE MATERIALS OTHER THAN

DECORATIVE VEGETATION IN NEW AND

EXISTING BUILDINGS……………………………….……..Page   8

SECTION 901       FIRE PROTECTION SYSTEMS – GENERAL ..………………...…..Page   8

SECTION 902       DEFINITIONS………………………………………………………...Page   8

SECTION 903       AUTOMATIC SPRINKLER SYSTEMS……………………..............Page   9

SECTION 904	 ALTERNATIVE AUTOMATIC FIRE-

EXTINGUISHING SYSTEMS…………………………………..Page 11

SECTION 905       STANDPIPE SYSTEMS………………………………………………Page 12

SECTION 906       PORTABLE FIRE EXTINGUISHERS……………………………… .Page 12

SECTION 907       FIRE ALARM AND DETECTION SYSTEMS………………………Page 13

SECTION 908       EMERGENCY ALARM SYSTEMS………………………………….Page 15

SECTION 909       SMOKE CONTROL SYSTEMS………………………………………Page 15

SECTION 912       FIRE DEPARTMENT CONNECTIONS……………………...............Page 16

SECTION 913       FIRE PUMPS…………………………………………………………..Page 16

SECTION 914	  FIRE PROTECTION BASED ON SPECIAL DETAILED

REQUIREMENTS OF USE AND OCCUPANCY………………….Page 16

SECTION 1003     GENERAL MEANS OF EGRESS…………………………………….Page 16

SECTION 1006     MEANS OF EGRESS ILLUMINATION……………………………..	Page 16

SECTION 1007     ACCESSIBLE MEANS OF EGRESS………………………………...Page 17

SECTION 1008     DOORS, GATES AND TURNSTILES……………………………….Page 17

SECTION 1011     EXIT SIGNS…………………………………………………………...Page 18

SECTION 1013     GUARDS………………………………………………………………	Page 18

SECTION 1027     MEANS OF EGRESS FOR EXISTING BUILDINGS………………..	Page 18

SECTION 1405     FLAMMABLE AND COMBUSTIBLE LIQUIDS……………………	Page 18

SECTION 1417     SAFEGUARDING ROOFING OPERATIONS……………………… Page 18

SECTION 1504     SPRAY FINISHING…………………………………………..............	Page 19

SECTION 2404     TEMPORARY AND PERMANENT TENTS,

CANOPIES AND MEMBRANE STRUCTURES…………………..Page 19

SECTION 2701     HAZARDOUS MATERIALS – GENERAL PROVISIONS…………..Page 19

SECTION 3301     EXPLOSIVES AND FIREWORKS – GENERAL …………................Page 19

SECTION 3302     EXPLOSIVES AND FIREWORKS – DEFINITIONS...........................Page 19

SECTION 3308     FIREWORKS DISPLAY.........................................................................Page 20

SECTION 3309     TEMPORARY STORAGE OF CONSUMER FIREWORKS………....Page 20

APPENDIX A         BASIC FIRE CONTROL MEASURES………………………………Page 21

APPENDIX B         CENTRAL STICKNEY FIRE PROTECTION DISTRICT FIRE

ALARM PLAN SUBMITTAL CHECKLIST……………………..Page 22

APPENDIX C         CENTRAL STICKNEY FIRE PROTECTION DISTRICT SPRINKLER

SYSTEM PLAN SUBMITTAL CHECKLIST ……...……………..Page 24

APPENDIX E         CENTRAL STICKNEY FIRE PROTECTION DISTRICT WRITTEN

REQUEST FOR RECORDS…………………………………..……Page 26

Attachment A           REFERENCED CODES AND STANDARDS……………………...	Page 27

Attachment B            FEES……………………………… ………………………………... Page 28

SECTION 101

ADMINISTRATION - general

101.1 is amended to read as follows:

101.1 Title.  These regulations shall be known as the Fire Code of Central Stickney Fire Protection District, hereinafter referred to as "this code."

101.2.2 is added to read as follows:

101.2.2 Name Change.  Any where in this code where the term “Fire Code Official” is used, it shall be changed to “Fire Prevention Code Official.”

101.5.1 is added to read as follows:

101.5.1 Conflicting Code Information.  In the event this code or any portion thereof shall be in conflict with another code or portion thereof on the same subject matter the more stringent code shall apply.

101.6 is added to read as follows:

101.6 NFPA Appendixes: The appendixes of all NFPA standards are to be considered as part of each standard and are considered “shall” requirements, not “should” information.

## SECTION 102

## APPLICABILITY

102.3 is amended to read as follows:

102.3 Change of use or occupancy.  A change of use or occupancy shall not be made to any building or tenant space without approval of the Code Official.  The Code Official shall certify that such building or tenant space meets the provisions of law governing building construction for the proposed new use or occupancy. The building is required to comply with the fire protection requirements of this code.

SECTION 104

GENERAL AUTHORITY AND RESPONSIBILITIES

104.6.5 is added to read as follows:

104.6.5 Written request for records. Any person wanting records from the Fire Prevention Bureau must submit in writing on the Central Stickney Fire Protection District Written Request for Records form. (Appendix E)

SECTION 105

PERMITS

105.3.6 is amended to read as follows:

105.3.6 Compliance With Code: All work preformed under a permit issued shall conform to the approved application and plans and any approved amendments thereto. It shall be unlawful for any owner, agent, architect, structural engineer, contractor, or builder engaged in erecting, altering, or repairing any structure or appurtenance thereof to make any departure from the drawing or plans as approved by the code official. Any of the requirements in this ordinance shall render the same void.

The Central Stickney Fire Protection District reserves the rights to send out any plan reviews to a third party agency because of the level of difficulty or availability of personal to perform the review. The third party agency shall invoice the permit holder directly for the services rendered.

105.3.6.1 is added to read as follows:

105.3.6.1 Compliance: No building or structure shall be constructed or occupied if said building or structure is not in compliance with this ordinance. An occupancy permit shall be issued by the code official in conjunction with the Cook County Building Inspector prior to occupancy when it is determined the building or structure has been constructed in compliance with this ordinance.

105.3.9 is added to read as follows:

105.3.9 Certificate of occupancy. The Code Official shall issue a certificate of occupancy only if, after inspection, he/she finds that such building or tenant space complies with the provisions of this Ordinance and all other Ordinances of the Central Stickney Fire Protection District, Cook County, and that said building or tenant space has been completed in accordance with the approved plans and documents filed in support of the Application for Building Permit relating to said building or tenant space.  Such Certificate shall show the permitted use for the building or tenant space.

In accordance with Attachment B (Fees), all outstanding fees shall be paid in full, prior to issuance of a certificate of occupancy by the Code Official.

105.4.4 is amended to read as follows:

105.4.4 Approved documents.  Construction documents approved by the fire code official are approved with the intent that such construction documents comply in all respects with this code.  Review and approval by the fire code official shall not relieve the applicant of the responsibility of compliance with this code.  Approval or disapproval shall be addressed in letter form and forwarded to the appropriate county or village building department having jurisdiction, stating reason(s) for disapproval or all requirements to be met prior to occupancy.

SECTION 106

INSPECTIONS

106.5 is added to read as follows:

106.5 Inspection and Enforcement process: In its efforts to ensure that fire protection safety for its residents and businesses of the Central Stickney Fire Protection District, the Fire Prevention Bureau shall inspect all buildings in the District for compliance with the fire safety codes of the District on a regular basis. The process by which the Bureau shall inspect and issue citations for failure to comply with the District fire safety codes shall be established by the Bureau S.O.P.

SECTION 108

BOARD OF APPEALS

108.1 is amended to read as follows:

108.1 Board of appeals established.  In order to hear and decide appeals of orders, decisions or determinations made by the code official relative to the application and interpretation of this code, there shall be and is hereby created a board of appeals consisting of members who are qualified by experience and training to pass on matters pertaining to this code and who are not employees of the jurisdiction.  The code official shall be an ex officio member of said board but shall have no vote on any matter before the board.  The board of appeals shall be the board of trustees of the Central Stickney Fire Protection District.  The board shall adopt rules of procedure for conducting its business, and shall render all decisions and findings in writing to the appellant with a duplicate copy to the code official.

SECTION 109

VIOLATIONS

109.3 is amended to read as follows:

109.3 Violation penalties.  Persons who shall violate a provision of this code or shall fail to comply with any of the requirements thereof or who shall erect, install, alter, repair or do work in violation of the approved construction documents or directive of the code official, or of a permit or certificate used under provisions of this code, shall be guilty of an ordinance violation, punishable by a fine of not less than fifty ($50.00) Dollars nor more than one ($1,000.00) thousand dollars, plus all legal fees and all costs caused by enforcement.  Such fees and costs shall include, but not limited to, staff costs of inspection or re-inspection, legal fees, and staff cost of enforcement.  Each day that a violation continues after due notice has been served shall be deemed a separate offense.

SECTION 110

UNSAFE BUILDINGS

110.5 is added to read as follows:

110.5 Fire watch.  Where conditions exist that are deemed hazardous to life and property by the code official, a fire watch shall be implemented.  The code official shall determine the number of personnel required and the duration necessary for the fire watch.  A fee of $75.00 per hour for each Central Stickney Fire Protection District personnel assigned to the fire watch shall be charged.  Conditions that may require a fire watch shall include, but are not limited to, the following:

- Newly constructed building opened for occupancy prior to completion of the fire safety equipment and supervision;

- Building in which the fire safety equipment and supervision is placed out-of-service and will not be restored within two (2) hours;

- Building with an occupancy load greater than the posted numbers;

- Special programs or vents where there will be space for standing room over the seating area and the exits will handle both seated and standing people; and

- Situations where the fire-load is greater than the normal day-to-day operation.

SECTION 111

STOP WORK ORDER

111.4 is amended to read as follows:

111.4 Failure to comply.  Any person who shall continue any work after having been served with a stop work order, except such work as that person is directed to perform to remove a violation or unsafe condition, shall be liable to a fine of not less than fifty ($50.00) dollars or more than one ($1,000.00) thousand dollars.

SECTION 202

GENERAL DEFINITIONS

Board of Trustees is added to read as follows:

BOARD OF TRUSTEES: The corporate authorities of the Central Stickney Fire Protection District.

Building is added to read as follows:

BUILDING: Any structure used or intended for supporting or sheltering any use of occupancy.

Building Code is added to read as follows:

BUILDING CODE: The Building Code and its amendments as adopted by the Trustees of the Central Stickney Fire Protection District.

Certificate of Use and Occupancy is added to read as follows:

CERTIFICATE OF USE AND OCCUPANCY. The certificate issued by the Code Official which, permits the use of a building or tenant space in accordance with the approved plans and specifications and which certifies compliance with the provisions of law for the use and occupancy of the building or tenant space in its several parts together with any special stipulations or conditions of the building permit.

Change of Occupancy is amended to read as follows:

CHANGE OF OCCUPANCY. The change in purpose for which a building or part thereof is used or intended to be used including a change in tenants or tenant space.

Change of Use is added to read as follows:

CHANGE OF USE. An alteration by change of use in a building or tenant space heretofore existing to a new use group which imposes other special provisions of law governing building construction, equipment or means of egress.

Code Official is added to read as follows:

CODE OFFICIAL: The designated Fire Marshal of the Central Stickney Fire Protection District and or his/her subordinates.

Fire Watch is amended to read as follows:

FIRE WATCH. A temporary measure intended to ensure continuous and systematic surveillance of a building or portion thereof by one or more qualified Central Stickney Fire Protection District personnel, for the purpose of identifying and controlling fire hazards, detecting early signs of unwanted fire, and raising an alarm of fire and notifying the fire department.

SECTION 307

OPEN BURNING AND RECREATIONAL FIRES

307.4.1 is amended to read as follows:

307.4.1 Bonfires.  A bonfire shall not be conducted within 50 feet of a structure or combustible material. Conditions which could cause said fire to spread to within 50 feet of a structure or combustible material shall be eliminated prior to ignition.  Bonfires shall not exceed 4 feet in diameter and/or 16 square feet.  Bonfires may only contain cut, natural wood.

307.4.2 is amended to read as follows:

307.4.2 Recreational fires.  Recreational fires shall not be conducted within 25 feet of a structure or combustible material.  Conditions which could cause a fire to spread within 25 feet of a structure or combustible material shall be eliminated prior to ignition.  Recreation fires shall be contained in a manufactured, outdoor fireplace/pit.  Containers for recreational fires shall be no greater than 30 inches in diameter and/or 6.25 square feet.  Recreation fires may only contain cut, natural wood that will fit within the confines of the container.

SECTION 308

OPEN FLAMES

308.3.1.1 is amended to read as follows:

308.3.1.1 Liquefied petroleum gas-fueled devices.  LP gas burners having an LP gas container with a water capacity of greater than 2 pounds shall not be located on combustible balconies or within 10 feet of combustible construction.  The storage of LP gas containers shall be prohibited on balconies or on any inside portion of apartment buildings, condos, stacked units or other structures with similar occupancies.

SECTION 309

POWERED INDUSTRIAL TRUCKS AND EQUIPMENT

309.4 is amended to read as follows:

309.4 Fire extinguishers.  Battery charging areas shall be provided with a fire extinguisher complying with section 906 having a 4A60BC rating within 20 feet of the battery charger.

SECTION 311

VACANT PREMISES

311.2.2 is amended to read as follows:

311.2.2 Fire Protection.  Fire alarm, sprinkler and standpipe systems shall be maintained in an operable condition at all times.

Exception 1 & 2 is deleted.

311.2.4 is added to read as follows:

311.2.4 Fire Protection Up Grades: Any building that is vacant more that 30 days or were change of occupancy occurs shall comply with this ordinance before any use of occupancy will be granted.  All requirements shall comply with section 907.2.

SECTION 312

VEHICLE IMPACT PROTECTION

312.4 is added to read as follows:

312.4 Gas Meter Protection: Where deemed necessary by the fire code official, guards shall be installed around gas meters to provide protection against vehicular damage.

SECTION 404

FIRE SAFETY AND EVACUATION PLANS

404.2 is amended to read as follows:

404.2 Where required. An approved fire safety and evacuation plan shall be prepared and maintained for all occupancies and buildings as required by the code official.

SECTION 503

FIRE APPARATUS ACCESS ROADS

503.1 is amended to read as follows:

503.1 Where required. Fire apparatus access roads shall be provided and maintained in accordance with sections 503.1.1- 503.1.3.  The Fire Prevention Code Official shall require and designate public and private fire lanes as deemed necessary for effective and efficient operation of fire apparatus.

Exception 1 to 503.1.1 is deleted.

503.1.1.1 is added to read:

503.1.1.1 Public/Private access for fire apparatus.  Public or private access, for all occupancy classification with the exception of R-3 shall be provided for fire apparatus when the building is three stories or higher.  Fire lane access for an aerial ladder and/or mechanically elevated mechanism shall be required to cover three-quarters of all exterior building walls.

503.2.1 is amended to read:

503.2.1 Dimensions.  The minimum width of fire lanes shall be 20 feet and an inside radius of 45 feet shall be provided to accommodate vehicles when turning.  The fire lanes shall be placed 25 feet from the building to the edge of the fire lane or 35 feet to the center of the fire lane to the building.  Public parking areas used as fire lanes shall have 25 feet to the rear of parking spaces to the building and 24 feet of open area to the rear of the parking spaces.  Fire lanes shall have an unobstructed vertical clearance of not less than 15 feet. The road shall be constructed with the capability to handle 80,000 pounds (weight of fire apparatus).

503.2.4 is amended to read:

503.2.4 Turning radius.  The required turning radius for a fire apparatus access road shall be determined by the Fire Prevention Code Official.  Fire lane turn around shall have an inside radius of 45 feet and shall have a driving area width of 27 feet in order to accommodate vehicles.

503.2.5 is amended to read as follows:

503.2.5 Dead ends.  Dead end fire apparatus access roads in access of 150 feet in length shall be provided with an approved area for turning around fire apparatus. All cul-de-sacs shall have a minimum diameter of 90 feet if parking is allowed

503.3.1 is added to read as follows:

503.3.1 Fire Lanes.  All fire lanes shall be posted with the appropriate signage.

SECTION 505

PREMISES IDENTIFICATION

505.1 is amended to read as follows:

505.1 Address numbers. New and existing buildings and tenant spaces shall have approved address numbers, building numbers or approved building identification placed in a position that is plainly legible and visible from the street or road fronting the property.  These numbers shall contrast with their background. Addresses on glass shall be white.  Address numbers shall be Arabic numerals or alphabet letters.  Exterior numbers shall be a minimum of 6 inches high.  Interior tenant spaces shall be a minimum 4-inch high numbers. Where access is by means of a private road and the building cannot be viewed from public way, a monument, pole, or other sign or means shall be used to identify the structure.

SECTION 506

KEY BOXES

506.1 is amended to read as follows:

506.1 When required.  All newly constructed buildings or tenant spaces are required to install an approved key box in an accessible location approved by the code official and shall contain keys and other items necessary to provide to the fire district access to the building at locked points of ingress and egress whether on the interior or exterior of such building, to include building systems, controls and devices, such as but not limited to: Fire alarm systems, automatic fire sprinkler systems, elevator controls, electrical rooms and mechanical rooms.

Exception:  Key boxes are not required for single-family detached dwellings, unless equipped with a fire sprinkler system.

506.1.2 is added to read as follows:

506.1.2 Type of key box.  The type of key box approved for use by the Central Stickney Fire Protection District is the Knox box brand key vault/rapid entry system.  The Central Stickney Fire Protection District shall be in complete control of key box and rapid entry system authorization and operation.  The Central Stickney Fire Protection District shall not be required to purchase or sell any key box or rapid entry system products.  The size of the required Knox box will be based upon the number of keys to be secured in the box and will be at the discretion of the Fire Prevention Code Official.

506.1.3 is added to read as follows:

506.1.3 Location and number: Knox box location. The installation location of the Knox box shall be approved by the Fire Code Official.  The Knox box shall be mounted at the height of six feet above the finished floor. The total number of Knox Boxes required shall be determined by the Code Official.

506.1.4 is added to read as follows:

506.1.4 Outside Strobe. A weatherproof clear outside strobe shall be installed over the Knox box. All outside strobes shall be 75 candela minimum.

506.3 is added to read as follows:

506.3 Electric shunt switch. An electric Knox shunt/shut off switch shall be required in buildings of all use groups with multiple electric panel rooms and/or buildings having an 800 ampere service or greater.

- Switch will be mounted next to main Knox, box or at a location specified by the fire code official.

- Switch should be mounted at a height of 6 (six) feet from the finished floor.

SECTION 507

FIRE PROTECTION WATER SUPPLIES

507.2.3 is added to read as follows:

507.2.3 Fire Hydrant Water Supply. The fire hydrants shall be on a domestic water system. The fire hydrant water supply shall be separate from the fire protection system water supply.

507.5.1 is amended to read as follows:

507.5.1 Where required. Fire hydrants shall be located along a fire apparatus access road so that no portion of a building or facility will be more than 300 feet from any hydrant.  Additional hydrants and mains shall be provided where required by the code official.

507.5.1.1 is added to read as follows:

507.5.1.1 Fire department connections. Hydrants shall be located within 75 feet to any fire department sprinkler or standpipe connection as determined by the code official. Delete exemption #2.

507.5.7 is added to read as follows:

507.5.7 Fire hydrant installation.  Fire hydrants shall be installed so that:

- Access:  Access to fire hydrants shall be by any approved roadway as specified by this code.

- Distance to Roadways:  Hydrants shall be located approximately ten (10) feet from all weather roadways.

- Pumper Outlet Direction:  Each hydrant shall have the pumper (steamer) connection facing the primary roadway and shall be accessible so that a connection can be made between the hydrant and the apparatus located in the street with twenty (20) feet of suction hose.

- Hydrant Outlet Location:  Fire hydrant outlets shall be a minimum of eighteen (18) inches and no more than thirty-six (36) inches above the finished grade.

- Hydrant Type:  Fire hydrants used in conjunction with water supplies shall be of a type acceptable to the Central Stickney Fire Protection District.

SECTION 508

FIRE COMMAND CENTER

508.1.6 is added to read as follows:

508.1.6 Mall Fire Command Station: A fire command station for fire department operations shall be provided in a location approved by the fire department. The fire command station shall contain: the voice/alarm signaling system controls; the fire department communication system controls; the automatic fire detection and alarm system annunciator panels; an annunciator that visually indicates the floor location of the elevators and weather they are in operational; status indicators and controls air handling systems; sprinkler valve and water flow detector display panels; and a public telephone system.

SECTION 509

FIRE DEPARTMENT ACCESS TO EQUIPMENT

509.2 is added to read as follows:

509.2 Access to fire equipment. In multiple single-family dwellings where there is no common area, fire alarm panels and sprinkler system valves shall be located in a room accessible only to fire district personnel from the exterior of the building. The fire department shall have access at any time to such equipment without entering an individual dwelling unit.

SECTION 511

EMERGENCY NOTIFICATION

511.1 is added to read as follows:

511.1 Emergency notification.  It shall be the responsibility of the property owner and/or manager to provide current contact persons and telephone numbers of persons to be notified in case of an emergency involving their property and/or building.

SECTION 607

ELEVATOR RECALL AND MAINTENANCE

607.1.1 is added to read as follows:

607.1.1  Automatic elevators for fire department use.  One elevator to be installed in all new buildings shall be sized for stretcher use by the fire department.  Minimum size to be 4000 pounds with a clear inside dimension of 7’ wide x 4’3” deep with a 42” side slide door.

607.5 is added to read as follows:

607.5 Elevator phone. All required emergency elevator phones shall directly dial the Central Stickney Fire Protection District's Communications Center via the phone number designated by the code official.

SECTION 609

COMMERCIAL KITCHEN HOODS

609.4 is added to read as follows:

609.4  Hood system suppression. All hood and duct extinguishing systems shall comply with the U.L. Standard # 300 and be supervised by the buildings fire alarm system.

SECTION 806

DECORATIVE VEGETATION IN

NEW AND EXISTING BUILDINGS

806.1.1 is amended to read as follows:

806.1.1 Restricted occupancies.  Natural cut trees shall be prohibited in groups, A, B, E, I, M, R-1, R-2 and R-4.  Exception is deleted.

SECTION 807

DECORATIVE MATERIALS OTHER THAN DECORATIVE

VEGETATION IN NEW AND EXISTING BUILDINGS

Exceptions 1 and 2 to 807.4.3.1 are deleted.

Exceptions 1 and 2 to 807.4.4.1 are deleted.

SECTION 901

FIRE PROTECTION SYSTEMS - GENERAL

901.2.2 is added to read as follows:

901.2.2 Fire Alarm Installers. The Illinois Department of Regulation has the following requirements for alarm system installers:

- Private alarm contractor’s license, issued by the Department of Professional Regulation, is required for an individual to be able to install, repair or modify fire alarm systems.

- It is important to note the requirements allow an exemption from obtaining a “Private Alarm Contractor’s License if the fire alarm system work is performed by a “Licensed Electrical Contractor”.

901.9.1 is added to read as follows:

901.9.1 Materials and contents information. Construction documents for fire protection systems permit shall include information on the contents, the occupancy, the location and arrangement of the structure, and the contents involved, the exposure to any hazard, the extent of the system coverage, the suppression system design criteria, the supply and extinguishing agents, the location of any standpipes, and the location and method an operation of any detection and alarm devices.

SECTION 902

DEFINITIONS

Total Area is added to read as follows:

TOTAL AREA.  For purposes of calculating total square feet and fire areas, the total floor area includes mezzanines and basements contained within the surrounding exterior walls of the building on all floors and levels, which are added together.  The area included within the surrounding exterior walls of a building including roof overhangs, extensions, and all enclosed extensions, which are also added to the calculation. Areas of a building not provided with surrounding walls shall be included within the building area if such areas are included within the horizontal projection of the roof or floor above.  Interior walls, including fire walls, and party walls, shall not be considered as walls which divide a structure into two or more separate buildings, but a structure containing such interior walls shall be considered as one building for the purpose of this section.

SECTION 903

AUTOMATIC SPRINKLER SYSTEMS

903.2.1.1 is amended to read as follows:

903.2.1.1 Group A-1: An automatic sprinkler system shall be provided throughout all Group A-1 occupancies.

903.2.1.2 is amended to read as follows:

903.2.1.2 Group A-2: An automatic sprinkler system shall be provided throughout all Group A-2 occupancies.

903.2.1.3 is amended to read as follows:

903.2.1.3 Group A-3: An automatic sprinkler system shall be provided throughout all Group A-3 occupancies.

903.2.1.4 is amended to read as follows:

903.2.1.4 Group A-4: An automatic sprinkler system shall be provided throughout all Group A-4 occupancies.

903.2.1.5 is amended to read as follows:

903.2.1.5 Group A-5: An automatic sprinkler system shall be provided throughout all Group A-5 occupancies.

903.2.1.6 is added to read as follows:

903.2.1.6 All Group A Occupancies: Quick response sprinklers shall be provided throughout all Group A occupancies.

903.2.2 is added to read as follows:

903.2.2 Group B: An automatic sprinkler system shall be provided throughout all Group B occupancies.

903.2.3 is amended to read as follows:

903.2.3 Group E: An automatic sprinkler system shall be provided throughout all Group E occupancies.

903.2.4 is amended to read as follows:

903.2.4 Group F-1: An automatic sprinkler system shall be provided throughout all Group F-1 occupancies. Provide all spec warehouse buildings with a ceiling roof height of 25 feet or greater to be protected with an ESFR fire sprinkler system or a hydraulically calculated system for a class IV commodities with rack storage calculated to the greatest storage height.

903.2.5 is amended to read as follows:

903.2.5 Group H: An automatic sprinkler system shall be installed in all Group H occupancies.

903.2.5.1 is deleted.

903.2.5.2 is deleted.

Table 903.2.5.2 is deleted.

903.2.5.3 is deleted.

903.2.6 is amended to read as follows:

903.2.6 Group I: An automatic sprinkler system shall be installed in all Group I occupancies, INCLUDING ALL:  Group homes, half-way houses, residential board and care facilities, congregate care facilities, assisted living facilities, alcohol and drug centers and social rehabilitation facilities, regardless of the number of persons occupying such buildings.

903.2.7 is amended to read as follows:

903.2.7Group M: An automatic sprinkler system shall be installed in all Group M occupancies.

903.2.7.1 is deleted.

903.2.8 is amended to read as follows:

903.2.8 Group R: An automatic sprinkler system shall be installed in all Group R occupancies.

903.2.9 is amended to read as follows:

903.2.9 Group S-1: An automatic sprinkler system shall be installed in all Group S-1 occupancies.

903.2.9.1 is amended to read as follows:

903.2.9.1 Repair garages. An automatic sprinkler system shall be installed in all repair garage occupancies.

903.2.9.2 is amended to read as follows:

903.2.9.2 Bulk storage of tires. An automatic sprinkler system shall be installed in all Bulk Storage of Tires buildings.

903.2.10 is amended to read as follows:

903.2.10 Group S-2. An automatic sprinkler system shall be provided throughout all buildings classified as a parking garage.

903.2.10.1 is amended to read as follows:

903.2.10.1 Commercial parking garages. An automatic sprinkler system shall be provided throughout all buildings used for storage of commercial trucks, trailers, transport container units or buses.

The exception to 903.2.11 is deleted.

903.2.11.1 is amended to read as follows:

903.2.11.1 Stories and basements without openings. An automatic sprinkler system shall be installed without openings.

903.2.11.1.2 is amended to read as follows:

903.2.11.1.2 Openings on one side only. Where openings in a story are provided on only one side and the opposite wall of such story, the story shall be equipped throughout with an automatic sprinkler system.

903.2.11.1.3 is amended to read as follows:

903.2.11.1.3 Basements. All basements shall be equipped throughout with and approved automatic sprinkler system.

903.3.1 is amended to read as follows:

903.3.1 Standards: Sprinkler systems shall be designed and installed in accordance with sections 903.3.1.1 through 903.3.1.3. All sprinkler piping material is to be approved metallic piping.  Plastic pipe is not allowed for sprinkler pipe material except for an R-3 use group.

903.3.1.1.1 is deleted.

903.3.1.2 is amended to read as follows:

903.3.1.2 NFPA 13R Sprinkler systems. Automatic sprinkler systems in Group R occupancies up to and including three stories in height shall be installed in accordance with NFPA 13R. An addressable fire alarm system shall be installed as required by the Central Stickney Fire Protection District.

903.3.1.3 is amended to read as follows:

903.3.1.3 NFPA 13D Sprinkler systems: Automatic sprinkler systems shall be installed throughout one-and two-family dwellings and townhouses in accordance with NFPA 13D.

903.3.5 is amended to read as follows:

903.3.5 Water supplies. Water supplies for automatic sprinkler systems shall comply with this section and the standards referenced in Section 903.3.1. The potable water supply shall be protected against backflow in accordance with the requirements of this section and the International Plumbing code and the Illinois Plumbing Code.

903.3.5.1 is amended to read as follows:

903.3.5.1 Water Supply: The fire protection water supply system that shall be utilized is the underground loop ran by the 51st Water Association. The fire protection water supply shall be separate from the domestic water supply. Provide separate lead-ins from the public water main.

903.3.5.3 is added to read as follows:

903.3.5.3 Safety factor. Hydraulically calculated sprinkler systems shall maintain a minimum of 10% or five (5) pounds per square inch cushion (whichever is greater) between the seasonal low water supply and the total sprinkler demand. The total sprinkler demand shall include the sprinkler demand and the hose stream demand. The flow data used in these calculations shall be no more than one year old.

903.3.5.4 is added to read as follows:

903.3.5.4 Multi tenant occupancy. When an automatic fire suppression system is installed in a multi tenant building, each tenant shall have its own sprinkler supply line off the main or riser with its own water flow switch and control valve. A strobe light shall be mounted on the exterior front of that tenant space and as indicated in Section 903.4.  The strobe light shall activate upon water flow and/or fire alarm activation within the individual unit.

903.3.7 is amended to read as follows:

903.3.7  Fire department connections. The location of the fire department connection shall be approved by the fire prevention code official.  The fire department connection shall consist of one five inch Storz coupling on a 30 degree elbow mounted between 36 inches and 48 inches above the finished floor.

Exceptions 2, 4 and 5 to 903.4 are deleted.

903.4.1 is amended to read as follows:

903.4.1 Signals. Alarm, supervisory and trouble signals shall be distinctly different and shall be directly connected to the communications center of the Central Stickney Fire Protection District in a method approved by the Fire Prevention Code Official as defined in NFPA 72.

903.4.2.1 is added to read as follows:

903.4.2.1 Sprinkler Alarms: Approved combined audible/visual devices shall be connected to every fire protection suppression system. Such alarm devices shall be activated by the systems operation. Devices shall be located:

- On the outside wall above each Fire Department Connection

- Throughout all areas, and floors inside the building.

903.4.3.1 is added to read as follows:

903.4.3.1 Multiple Story Buildings: In multiple story buildings, provide floor control valves with water flow switches for each floor. No birdcage systems are allowed.

903.4.3.2 is added to read as follows:

903.4.3.2 Floor Plan: A diagram showing area served by each system and/or control valves shall be submitted. The same diagram shall be placed adjacent to the risers.

903.4.4 is added to read as follows:

903.4.4 Hydraulic Calculations: By each hydraulically calculated area, on each drawing, provide a copy of the hydraulic nameplate.

903.4.5 is added to read as follows:

903.4.5 Fire Pumps: All fire pumps shall have an outside test header. Provide an OS&Y gate valve on all fire pump test headers. Provide a ball drip between the OS&Y control valve and the outside test header. The test header shall have the minimum 2½” test valves required by NFPA 20.

903.5.1 is added to read as follows:

903.5.1 Inspectors Test Vales: Fire sprinkler system inspectors test valves shall be accessible at all times and located no more than 6 feet above the finished floor. On multiple riser systems test valves shall be marked as to which riser and area it tests and shall be located at the furthest point of the system.

SECTION 904

ALTERNATIVE AUTOMATIC FIRE-EXTINGUISHING SYSTEMS

904.3.5 is amended to read as follows:

904.3.5 Monitoring. All automatic fire extinguishing systems shall be monitored by a fire alarm system directly connected to the communications center of the Central Stickney Fire Protection District, in a method approved by the Code Official in accordance with NFPA 72.

SECTION 905

STANDPIPE SYSTEMS

905.2.1 is added to read as follows:

905.2.1 Standpipe System Design: standpipe systems in connection with an approved hydraulically calculated sprinkler system shall maintain a minimum of 10% pressure cushion between the seasonal low water supply and the total standpipe demand.

905.3.1 is amended to read as follows:

905.3.1 Height: Class I standpipe systems shall be installed throughout all buildings two (2) or more stories in height. All standpipe systems shall be automatic wet systems.

905.3.1.1 is added to read as follows:

905.3.1.1 Building area. Class I standpipe systems shall be installed in all buildings where any portion of the building's interior area is more than 150 feet of travel, vertically, and horizontally, from the main entrance of the building of fire department vehicle access.  Where the most remote portion of a floor or story is more than 150 feet from a hose connection, the Fire Prevention Code official may require that additional hose connections be provided in approved locations.

905.3.1.2 is added to read as follows:

905.3.1.2: System Required: Buildings required by section 905.3 to be equipped with standpipe systems shall be provided with a wet standpipe system that complies with section 905.3.1.

905.3.1.3 is added to read as follows:

905.3.1.3High Rise Buildings: High rise building standpipes shall be designed for a minimum 65 psi to 100 psi at 500 gpm to the highest most remote standpipe outlet. Provide a minimum 250 gpm for each additional standpipe riser. The total shall not be required to exceed 1,250 gpm.

905.3.1.4 is added to read as follows:

905.3.1.4 Open Parking Structures: Detached open parking structures shall be provided with a dry standpipe system without a connection to the public water main. Attached open parking structures shall be provided with an automatic wet or automatic dry standpipe system.

905.12 is added to read as follows:

905.12 Pressure-Regulating Devices: Where residual pressure at any standpipe hose outlet exceeds 100 psi approved pressure-regulating devices shall be installed at the outlets to limit the pressure to 100 psi. Such devices shall regulate pressure under flow and no flow conditions. The pressure on the inlet side of the pressure-regulating device shall not exceed the rated working pressure of the device. All standpipe valves shall be Potter-Roemer, Inc. or equivalent emergency field adjustable pressure restricting 2½” angle valves, model 4085.

SECTION 906

PORTABLE FIRE EXTINGUISHERS

The exception to 906.1(1) is deleted.

906.3 is amended to read as follows:

906.3 Size and distribution. The minimum size fire extinguisher for use in all occupancy groups shall be 4A60BC. All other applications shall be in accordance with the provisions of NFPA 10.

906.4.1 is added to read as follows:

906.4.1 In areas with a wet chemical fire suppression system shall have a minimum of one 6 (six) liter wet chemical potassium based fire extinguisher within the kitchen area in addition to other required extinguishers.  Additional extinguishers may be required by the fire code official.

906.5.1 is added to read as follows:

906.5.1   Fire extinguishers shall be located within 5 feet of each exit door.  All other areas shall have fire extinguishers installed in accordance with NFPA 10.

SECTION 907

FIRE ALARM AND DETECTION SYSTEMS

907.1.4 is added to read as follows:

907.1.4 Underwriters laboratory certificates.  All Fire Alarm systems installed within the jurisdiction of the Central Stickney Fire Protection District shall be Underwriters Laboratory Certified as Remote Station type systems.  This Underwriters Laboratory certification shall remain in place for as long as a fire alarm system is required to be installed in the property. This shall also include those systems that monitor automatic sprinkler systems.

907.1.5 is added to read as follows:

907.1.5 Underwriters laboratory certificates existing systems.  Any existing systems will be required to be UL Certified within 5 years from the effective date of this ordinance. When an occupancy changes, a UL Remote Station certificate will also be required.  Where systems are upgraded, a UL Remote Station is also required, this would include new control panels and changes or additions to systems that are equal to or greater that 10% of the existing system.

907.1.6 is added to read as follows:

907.1.6 UL fire alarm installation requirements.  In order to install a fire alarm system in the Central Stickney Fire Protection District the installer must be a Licensed Fire Alarm Installer or a licensed electrician. Prior to acceptance testing, the alarm contractor that will be issuing the certificate for the Protected Property shall provide a current copy of the Alarm Contractor’s Certificate of Compliance to the Central Stickney Fire Protection District’s Fire Prevention Bureau.  A copy of the Protected Property’s Remote Station UL Certificate shall be provided to the Central Stickney Fire Protection District Fire Prevention Bureau upon completion of the acceptance test.

907.1.7 is added to read as follows:

907.1.7 Where required-existing buildings and structures. All existing commercial and multi tenant occupancy structures within the Central Stickney Fire Protection District shall have a working fire alarm system which is connected to the Communication Center of the Central Stickney Fire Protection District.  The master fire alarm panel in facilities/buildings that are rented or leased are the responsibility of the building owner to maintain and service.  For all commercial buildings that do not have a fire alarm system installed there will be a five year installation period, which shall allow building owners to comply. Any building that is vacant more that 30 days or were change of occupancy occurs shall comply with this requirement before any use of occupancy will be granted.  All requirements shall comply with section 907.2.

907.2 is amended to read as follows:

907.2 Where required-new buildings and structures. An approved manual, automatic or manual and automatic fire alarm system installed and maintained in accordance with the provisions of this code and NFPA 72 shall be provided in new buildings and structures in accordance with Section 907.2.1 through 907.2.23 and provide occupant notification in accordance with section 907.10, unless other requirements are provided by another section of this code. All fire alarm systems shall be an addressable type; and the fire alarm control panel or fully functional annuciator panel with no pass codes shall be installed within 10’ of the main entrance or in a location approved by the fire department. Multi-tenant buildings will be “ring by tenant” and shall include a weatherproof clear outside strobe over the entrance to each tenant space as directed by the Fire Code Official. All outside strobes shall be 75 candela minimum. Where automatic sprinkler protection installed in accordance with Section 903.3.1.1 or 903.3.1.2 is provided and connected to the building fire alarm system, automatic heat detection required by this section shall not be required.  All fire alarm wiring for the systems shall be encased in RED electrical metallic tubing (conduit).

907.2.1 is amended to read as follows:

907.2.1 Group A. A manual fire alarm system shall be installed and directly connected to the Communication Center of the Central Stickney Fire Protection District, in a method approved by the Code Official in accordance with NFPA 72 in all Group A occupancies.

907.2.2 is amended to read as follows:

907.2.2 Group B. A manual fire alarm system shall be installed and directly connected to the Communication Center of the Central Stickney Fire Protection District, in a method approved by the Code Official in accordance with NFPA 72 in Group B occupancies.

907.2.3 is amended to read as follows:

907.2.3 Group E. A manual fire alarm system shall be installed and directly connected to the Communication Center of the Central Stickney Fire Protection District, in a method approved by the Code Official in Group E occupancies.

907.2.4 is amended to read as follows:

907.2.4 Group F. A manual fire alarm system shall be installed and directly connected to the Communication Center of the Central Stickney Fire Protection District, in a method approved by the Code Official in accordance with NFPA 72 in Group F occupancies.

907.2.5 is amended to read as follows:

907.2.5 Group H. A manual fire alarm system shall be installed and directly connected to the Communication Center of the Central Stickney Fire Protection District, in a method approved by the Code Official in accordance with NFPA 72 in Group H occupancies.

907.2.6 is amended to read as follows:

907.2.6 Group I. A manual fire alarm system shall be installed and directly connected to the Communication Center of the Central Stickney Fire Protection District, in a method approved by the Code Official in accordance with NFPA 72 in Group I-1 occupancies.

Exception 1 to 907.2.6.1 is deleted.

907.2.6.2 is amended to read as follows:

907.2.6.2 Group I-2. A manual fire alarm system shall be installed and directly connected to the Communication Center of the Central Stickney Fire Protection District, in a method approved by the Code Official in accordance with NFPA 72 in Group I-2 occupancies.

907.2.6.3 is amended to read as follows:

907.2.6.3 Group I-3. A manual fire alarm system shall be installed and directly connected to the Communication Center of the Central Stickney Fire Protection District, in a method approved by the Code Official in accordance with NFPA 72 in Group I-3 occupancies.

907.2.7 is amended to read as follows:

907.2.7 Group M. A manual fire alarm system shall be installed and directly connected to the Communication Center of the Central Stickney Fire Protection District, in a method approved by the Code Official in accordance with NFPA 72 in Group M.

907.2.8 is amended to read as follows:

907.2.8 Group R-1. A manual fire alarm system and an automatic fire detection system shall be installed and directly connected to the Communication Center of the Central Stickney Fire Protection District, in a method approved by the Code Official in accordance with NFPA 72 in all Group R-1 occupancies.

907.2.9 is amended to read as follows:

907.2.9 Group R-2. An automatic fire alarm system shall be installed and directly connected to the Communication Center of the Central Stickney Fire Protection District, in a method approved by the Code Official in accordance with NFPA 72 in all Group R-2 occupancies.

907.2.10 is amended to read as follows:

907.2.10 Group R-4. An automatic fire alarm system shall be installed and directly connected to the Communication Center of the Central Stickney Fire Protection District, in a method approved by the Code Official in accordance with NFPA 72 in all Group R-4 occupancies.

907.2.10.1.1 is added to read as follows:

907.2.10.1.1 Additional Detection: Heat detectors with audible devices shall be provided in all attached garages with residential occupancies. The heat detector shall transmit a signal to all other detection devices and all devices shall go into alarm with an audible signal.

907.2.11.2 is amended to read as follows:

907.2.11.2 Group I-1. Single or multiple-station smoke alarms shall be installed and maintained in sleeping areas in occupancies in Group I-1.

907.2.11. 2.1is added to read as follows:

907.2.11.2.1 Group S. A manual fire alarm system shall be installed and directly connected to the Communication Center of the Central Stickney Fire Protection District, in a method approved by the Code Official in accordance with NFPA 72 in Group S occupancies.

907.2.13 is amended to read as follows:

907.2.13 High-rise buildings.  Buildings with a floor used for human occupancy located more than 60 feet above the lowest level of fire department vehicle access shall be provided with an automatic fire alarm system, pressurized stairwells, fire command center, fire department communication center and an emergency voice/alarm communication system in accordance with Section 907.2.12.2

907.7.2 is amended to read as follows:

907.7.2 Power supply.  The primary and secondary power supply for the fire alarm shall be provided in accordance with NFPA 72. The secondary supply shall be equipped with a 60 hour battery.

907.7.3 is amended to read as follows:

907.7.3 Zones.  Each floor shall be zoned separately and a zone shall not exceed 10,000 square feet. The length of any zone shall not exceed 200 feet in any direction; a zoning indicator panel and the associated controls shall be provided in an approved location. The visual zone indication shall lock in until the system is reset and shall not be cancelled by the operation of a public alarm - silencing switch. A separate zone by floor shall be provided for the following types of alarm initiating devices where provided:

A. Detection devices.

B. Sprinkler water-flow alarms.

C. Manual fire alarm boxes.

D. Each tenant space in multi-tenant occupancies, and

E. Other approved type of automatic fire detection devices or suppression systems.

907.4.1 is amended to read as follows:

907.4.1 Duct smoke detectors. Duct smoke detectors shall be connected to the building’s fire alarm control panel when a fire alarm system is provided.  Activation of a duct smoke detector shall initiate a visible and audible fire signal and shut down the individual units. Duct smoke detectors shall not be used as a substitute for required open area detection.  Duct smoke detectors shall be required in all air handling units 2000 CFM or greater.

All test switches shall be labeled and installed in a proximate area near the Fire Alarm panel or as determined by the Fire Prevention Code Official.  All duct detectors should be labeled in correlation with the HVAC units and clearly marked on the inside ceiling, visible from the floor.  All rooftop units will be visibly marked from the roof/scuttle access point.

907.4.3.1  is added to read as follows:

907.4.3.1 Elevator emergency telephones. Elevator emergency telephones shall be connected to the Central Stickney Fire Protection District Communications Center.

907.9.6 is added to read as follows:

907.9.6 Records of completion.  A record of completion in accordance with NFPA 72 verifying that the system has been installed with the approved plans and specifications shall be provided.  A schematic minimum of and 8.5 by 11 inch shall be provided showing all devices and components of the alarm system.

SECTION 908

EMERGENCY ALARM SYSTEMS

908.1 is amended to read as follows:

908.1 Group H Occupancies. Emergency alarms for the detection and notification of an emergency condition in Group H occupancies shall be provided as required in Chapter 27. All required alarms shall be directly connected to the Communication Center of the Central Stickney Fire Protection District, in a method approved by the Code Official in accordance to provisions of NFPA 72.

SECTION 909

SMOKE CONTROL SYSTEMS

909.20.6 is added to read as follows:

909.20.6 In garage settings where a carbon monoxide detection device controls the activation of an exhaust system this system must shut down upon the activation the fire detection and/or suppression systems.  This will have a manual override control which will be installed under direction of the Fire Prevention Code Official.

909.20.6.1 is added to read as follows:

909.20.6.1 This system is subject to acceptance and testing by the Fire Prevention Code Official.

SECTION 912

FIRE DEPARTMENT CONNECTIONS

912.1.1 is added to read as follows:

912.1.1 Storz connection. The location of the fire department connection shall be approved by the fire prevention code official.  The fire department connection shall consist of one five inch Storz coupling on a 30 degree elbow downturn mounted between 36 inches and 48 inches above the finished floor.

912.2 is amended to read as follows:

912.2 Location. With respect to hydrants, driveways, buildings and landscaping, fire department connections shall be so located that fire apparatus and hose connected to supply the system will not obstruct access to the buildings for other fire apparatus. Fire department connections shall be located within 75 feet of a fire hydrant at a location approved by the code official.

912.5 is amended to read as follows:

912.5  Backflow protection. The potable water supply to automatic sprinkler and standpipe systems shall be protected against backflow as required by the International Plumbing Code and The Illinois Plumbing Code.

SECTION 913

FIRE PUMPS

913.4 is amended to read as follows:

913.4 Valve supervision. Where provided, the fire pump suction, discharge and bypass valves, and the isolation valves on the backflow prevention device or assembly shall be supervised by a fire alarm system directly connected to the Communication Center of the Central Stickney Fire Protection District, in a method approved by the Code Official in accordance with the provisions of NFPA 72.

SECTION 914

FIRE PROTECTION BASED ON SPECIAL DETAILED

REQUIREMENTS OF USE AND OCCUPANCY

The exception to 914.2.1(2) is deleted.

The exceptions to 914.3.1 are deleted.

The exception to 914.4.1 is deleted.

The exception to 914.7.1 is deleted.

SECTION 1003

GENERAL MEANS OF EGRESS

1003.1 is amended to read as follows:

1003.1	Applicability. The general requirements specified in this section shall apply to all three elements of the means of egress system, in addition to those specific requirements for the exit access, the exit and the exit discharge detailed elsewhere in this chapter.  The provisions of Chapter 34 of the International Building Code shall not be used to eliminate the installation requirements for exit signs and means of egress illumination systems.

SECTION 1006

MEANS OF EGRESS ILLUMINATION

The exceptions to 1006.1 are deleted.

The exception to 1006.2 is deleted.

1006.3 is amended to read as follows:

1006.3	Illumination emergency power.  The power supply for means of egress illumination shall normally be provided by the premise's electrical supply.

In the event of power supply failure, an emergency system shall automatically illuminate all of the following areas:

- Exit access corridors, passageways, and aisles in rooms and spaces, which require two or more means of egress.

- Exit access corridors and exit stairways located in buildings required to have two or more exits.

- Interior exit discharge elements, as permitted in Section 1006.1, in buildings required to have two or more exits.

- The portion of the exterior exit discharge immediately adjacent to exit discharge doorways in buildings required to have two or more exits.

- Conference rooms, training rooms, break or lunch rooms, and restrooms that accommodate more than one occupant.

SECTION 1007

ACCESSIBLE MEANS OF EGRESS

The exceptions to 1007.2.1 are deleted.

The exceptions to 1007.3 are deleted.

SECTION 1008

DOORS, GATES AND TURNSTILES

1008.1.9.3 is amended to read as follows:

1008.1.9.3 LOCKS AND LATCHES. Egress doors shall be readily open able from the egress side without the use of a key or special knowledge or effort.

Exceptions:

- Places of detention or restraint.

- Where approved by the code official, a readily visible durable sign is posted on the egress side on or adjacent to the door stating:  THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING IS OCCUPIED.  This sign shall be in letters 1 inch (25 mm) high on a contrasting background.

- Where egress doors are used in pairs, approved automatic flush bolts shall be permitted to be used, provided that the door leaf having the automatic flush bolts has no doorknob or surface mounted hardware.  The unlatching of any leaf shall not require more than one operation.

- Doors from individual dwelling units and guestrooms of Group R occupancies having an occupant load of 10 or less are permitted to be equipped with a night latch, dead bolt or security chain, provided such devices are accessible from the inside without the use of a key or tool.

SECTION 1011

EXIT SIGNS

Exception 2 to 1011.1 is deleted.

1011.1.2 is added to read as follows:

1011.1.2 Floor proximity exit signs. The installation of low-level exit signs to supplement regular exit signs shall be placed in all new occupancies to include places of assembly, hotels, department stores, or other buildings subject to transient occupancy and semi-permanent occupancy such as an apartment house, and as deemed necessary by the Fire Prevention Code Official.  Such exit signs may be approved luminescent, photo luminescent, self-luminous, or self-illuminated types. They are not intended to replace standard exit signs but are designed as a supplementary aid for a building occupant seeking egress in smoke-filled environment at a location that is the last to become obscured. Existing facilities shall be required to have this signage within 2 years.

Such signs shall be located near the floor level in addition to those signs required for doors or corridors. The bottom of the sign shall be not less than six (6) inches, but not more that eighteen (18) inches above the floor.  For exit doors, the sign shall be mounted on or adjacent to the door with the nearest edge of the sign within four (4) inches of the door frame.  Photo luminescent signs may be used in place of externally illuminated signs.

1011.1.3 is added to read as follows:

1011.1.3 Floor and stairwell signs. Floor and stairwell signs shall be required in all stairwells in every floor in all new construction and all existing hotels and nursing homes. Signs shall also be mounted on the wall adjacent to the door at five (5) foot above finished floor indicating floor level and stairwell designation.

1011.1.4 is added to read as follows:

1011.1.4 Floor proximity egress path marking.  Floor proximity exits signs are required in all use groups/occupancies as determined by the Fire Prevention Code Official.  Listed and approved floor proximity egress path marking that is internally illuminated shall be installed within eighteen (18) of the floor.  The system shall provide a visible delineation of the path of travel along the designated exit access and shall be essentially continuous, except as interrupted by doorways, hallways, corridors, or other such architectural features.  The system shall operate continuously or anytime the fire alarm system is activated.  Photo-luminescent path marking may be used in place of internally illuminated path markings.

# 1011.2 is amended to read as follows:

# 1011.2 Illumination: Exit signs should be internally, externally or photo luminescent illuminated.

SECTION 1013

GUARDS

Exception 6 to 1013.1 is deleted.

SECTION 1405

FLAMMABLE AND COMBUSTIBLE LIQUIDS

1405.7 is added to read as follows:

1405.7 Barrier protection/containment. Physical barriers shall consist of IDOT certified concrete barriers. Barriers shall be provided to protect the area where construction type fuel tanks are established. Containment will also be provided to contain 110% of the largest tanks capacity.

SECTION 1417

SAFEGUARDING ROOFING OPERATIONS

1417.3 is amended to read as follows:

1417.3 Fire Extinguishers for roofing operations.  Fire extinguishers shall be installed in accordance with section 906.  There shall be not less than one multi- purpose portable fire extinguisher with a minimum 4A60BC on the roof being covered or repaired.

SECTION 1504

SPRAY FINISHING

The exceptions to 1504.2 are deleted.

SECTION 2404

TEMPORARY AND PERMANENT TENTS,

CANOPIES AND MEMBRANE STRUCTURES

2404.12 is amended to read as follows:

2404.12 Portable fire extinguishers. Portable fire extinguishers shall be a 4A60BC extinguisher.

2404.14.1 is added to read as follows:

2404.14.1 Occupant load sign. A Sign with maximum occupant load must be prominently posted at the main entrance at all times.

SECTION 2701

HAZARDOUS MATERIALS – GENERAL PROVISIONS

2701.3.3.1 is amended to read as follows:

2701.3.3.1 Properties of hazardous materials. All buildings, and/or tenant spaces containing hazardous materials shall provide a Knox box document storage cabinet for placement of the MSDS sheets.  The box shall be large enough to accommodate all information.  It shall be mounted at 6 (six) feet above the finished floor, and shall be located in a spot that is approved by the fire prevention code official.

SECTION 3301

EXPLOSIVES AND FIREWORKS - GENERAL

Exceptions 2 and 4 to 3301.1.3 are deleted.

Exception 5 to 3301.1.3 is added to read as follows:

- Consumer Novelties.  The retail sale of approved consumer novelties shall be permitted.  Retail sales of consumer novelties shall be permitted in stores equipped with approved automatic sprinkler systems.  Displays of consumer novelties in retail stores shall be separated from exit doors by a minimum distance of twenty (20) feet.  The sale of consumer novelties shall not be permitted at mercantile occupancies that sell or dispense flammable or combustible liquids or gases.  Purchase of consumer novelties shall be restricted to those persons who are eighteen (18) years of age or older.  Approved consumer novelties include snakes or glow worm pellets, smoke devices, trick noisemakers known as party poppers, booby traps, snappers, trick matches, cigarette loads, auto burglar alarms, toy pistols, toy canes, toy guns, or other devices in which paper or plastic caps containing twenty-five hundredths grains or less of explosive compound are used, provided they are so constructed that the hand cannot come in contact with the cap when in place for the explosion; and toy pistol paper or plastic caps which contain less than twenty-five (25) hundredths grains of explosive mixture, the sale and use of which shall permitted at all times

SECTION 3302

EXPLOSIVES AND FIREWORKS - DEFINITIONS

Fireworks, 1.4G  is amended to read as follows:

Fireworks, 1.4G (Formerly known as Class C, Common Fireworks.) Small fireworks devices including hand-held wire sparklers containing restricted amounts of pyrotechnic composition designed primarily to produce visible or audible effects by combustion.  Such 1.4G fireworks which comply with the construction, chemical composition and labeling regulations of the DOT for Fireworks, UN 0336, and the U.S. Consumer Product Safety Commission as set forth in CPSC 16 CFR: Parts 1500 and 1507 are not explosive materials for the purpose of this code.

SECTION 3308

FIREWORKS DISPLAY

3308.1 is amended to read as follows:

3308.1 General. The display of fireworks, including proximate audience displays and pyrotechnic special effects in motion picture, television, theatrical, and group entertainment productions, shall comply with this chapter and 2010 edition of NFPA 1123 and/or 2006 edition of NFPA 1126.

3308.1.1 is added to read as follows:

3308.1.1 General requirements for all pyrotechnic/consumer fireworks displays. All pyrotechnic fireworks displays shall conform to the Fireworks Use Act (425 ILCS 35).

3308.2.1 is amended to read as follows:

3308.2.1 Outdoor displays. In addition to the requirements of Section 403 permit application for outdoor fireworks shall include a diagram of the location at which the display will be conducted including the site from which fireworks will be discharged; the location of buildings, highways, overhead obstructions and utilities; and the lines behind which the audience will be restrained.  All outdoor fireworks displays shall be electronically fired from an approved electronic firing unit.

3308.3.1 is added to read as follows:

3308.3.1 Pyrotechnic operator and licensing rules. Any person, company, entity, association, or corporation who distributes, provides display services or supervises a pyrotechnic display within the Central Stickney Fire Protection District must be licensed according to the Pyrotechnic Distributor and Operator Licensing Act (225ILCS 227).

3308.8.1 is added to read as follows:

3308.8.1 Fire department supervision of displays. All outside public fireworks displays are required to have a fire department standby, to be determined by the fire chief or his/her designee.  Fire department expenses incurred by this standby will be billed to the host of the display.  Local governmental agencies may be exempt from this fee.

3308.11 is added to read as follows:

3308.11 Retail display and sale. It shall be unlawful to sell, store, or advertise for sale, Division 1.4G, 1.3G & 1.4S fireworks within the boundaries of the Central Stickney Fire Protection District.

3308.12 is added to read as follows:

3308.12 Consumer fireworks.  Consumer fireworks (1.4G) as defined by the Fireworks Use Act (445 ILCS 35) shall not be manufactured, stored, sold retail or wholesale or utilized within the boundaries of the Central Stickney Fire Protection District along with the following unregulated items: sparklers of all sizes and types and smoke devices.

Appendices A, B, C, E, F and G are deleted.

SECTION 3309

TEMPORARY STORAGE OF CONSUMER FIREWORKS

3309.1 is deleted.

Appendix A is added to read as follows:

APPENDIX A

BASIC FIRE CONTROL MEASURES

A-101.1 Scope:  Adoption of fire control measures and regulations.  There has been adopted by the Central Stickney Fire Protection District fire control measures and regulations as herein set forth for the purposes of controlling conditions which could impede or interfere with fire suppression forces.

A-102.1 Authority at Fires and Other Emergencies: The Fire Official or duly authorized representatives, as may be in charge at the scene of a fire or emergency involving the protection of life and property, is empowered to direct such operations as may be necessary to extinguish or control any suspected or reported fires, gas leaks or other hazardous conditions or situations or of taking any other action necessary in the reasonable performance of their duty.  The Fire Official may prohibit any person, vehicle or object from approaching the scene and may remove or cause to be removed from the scene any person, vehicle, or object which may impede or interfere with the operations of the fire department.  The Fire Official may remove or cause to be removed any person, vehicle or object from the hazardous areas.  All persons ordered to leave a hazardous area shall do so immediately and shall not re-enter the area until authorized to do so by the Fire Official.

A-103.1 Interference with Fire District Operations: It shall be unlawful to interfere with, attempt to interfere with, conspire to interfere with, obstruct or restrict the mobility of or block the path of travel of any fire department emergency vehicle in any way, or to interfere with, attempt to interfere with, obstruct or hamper any fire department operation.

A-104.1 Compliance with Orders:  A person shall not willfully fail or refuse to comply with any lawful order or direction of the Fire Chief or to interfere with the compliance attempts of another individual.

A-105.1 Vehicles Crossing Fire Hose:  A vehicle shall not be driven or propelled over any unprotected fire hose of the fire department when laid down on any street, alleyway, private drive or any other vehicular roadway without the consent of the Fire Prevention Code Official in command of said operation.

A-106.1 Definition of Emergency Vehicle:  Authorized emergency vehicles shall be restricted to those which are defined and authorized under the laws of the State of Illinois.

A-107.1 Operation Of Vehicles on Approach of Authorized Emergency Vehicles:  Upon the approach of any authorized emergency vehicle, giving audible and visual signal, the operator of every other vehicle shall immediately drive the same to a position as near as possible and parallel to the right-hand edge or curb of the street or roadway, clear of any intersection and shall stop and remain in such position until the authorized emergency vehicle or vehicles shall have passed, unless otherwise directed by the Fire Official or a police officer.

A-108.1 Vehicles Following Fire Apparatus:  It shall be unlawful for the operator of any vehicle other than one on official business, to follow closer than 300 feet from any fire apparatus traveling in response to a fire alarm or to drive any vehicle within the block or immediate area where fire apparatus has stopped in answer to a fire alarm

A-109.1 Unlawful Boarding or Tampering With Fire District Emergency Equipment:  A person shall not without proper authorization from the Fire Official in charge of said fire department emergency equipment, cling to, attach himself to, climb upon or into, board or swing upon any fire department emergency vehicle, whether the same is in motion or at rest, or sound the siren, horn, bell or other sound-producing device thereon, or to manipulate or tamper with, or attempt to manipulate or tamper with any levers, valves, switches, starting devices, brakes pumps or other equipment.

A-110.1 Damage, Injury-Fire Department Equipment, and Personnel:  It shall be unlawful for any person to damage or deface, or attempt or conspire to damage or deface, any fire department emergency vehicle at any time or to injure, or attempt or conspire to injure, fire department personnel while performing departmental duties.

A-112.1 Blocking Fire Hydrants and Fire Department Connections:  It shall be unlawful to obscure from view, damage, deface, obstruct or restrict the access to any fire hydrant or any fire department connection for the pressurization of fire suppression systems, including fire hydrants and fire department connections located on public or private streets and access lanes or on private property. All vehicles blocking fire hydrants and fire department connections shall be moved immediately.

Appendix B is added to read as follows:

APPENDIX B

CENTRAL STICKNEY

FIRE PROTECTION DISTRICT

FIRE ALARM PLAN SUBMITTAL CHECKLIST

This checklist is an effort to help provide a uniform approach for the design community and to provide owners and fire alarm designers with complete fire alarm design and submittal package requirements.

When submitting plans for review all plan submittals must include this Fire Alarm Plan Submittal Checklist or they will not be accepted.  By completing this checklist and including all of the necessary information requested it is the intent of this document to provide efficient and appropriate turnaround of the plans submitted.  It is the responsibility of the installer/designer to assure that all applicable code requirements are followed. (Check with the Village Code to find the current standards.)

The installation, renovation, addition, and/or maintenance of any fire alarm system shall comply with the following:

IMPORTANT:

No installation work shall be performed until the plans have been reviewed and approved.

Expect up to 10 working days for plan reviews per submittal

CHECKLIST: (All plans submitted must contain the following)

- Proof of Contractor’s license to be able to work within the city limits of unincorporated Stickney Township. (UL Certified)

- Must be certified electrician to install Fire Alarm System, must be licensed to install Fire Alarm Systems.

FIRE ALARM DRAWINGS:

- Must submit Fire Alarm drawings to the Central Stickney Fire Protection District, Fire Prevention Bureau, 4951 S. Lotus Ave., Stickney Twp, IL 60638.  Any questions please contact the Bureau at 708-496-1268

- Must submit 3 complete sets of fire alarm drawings, and one on CD in PDF format, and cut sheet/product information.  The scaled drawings must include the following:

      - Title block to include the following information: Property name and address, Alarm Company name and address, date of drawing with space for revision dates, classification of the system per NFPA 72 1.3.1, who drew the drawing, the scale of the drawing, label the drawing as Fire Alarm System Standard or Addressable, Number of pages of the drawing.

      - A legend of Fire Alarm System located on one sheet to indicate the type of device installed.

      - A point-to-point wire diagram indicating the number of wires and gauge for each wire run.  Include EMT size when appropriate. Include a statement in the installation notes under the symbols legend indicating the type of wire and gauge for each circuit.

      - An on line and riser diagram for all devices, notification circuits, auxiliary circuits, initiating circuits, and circuit designation.

      - Include overall dimension of the building on each floor and square footage.  Ceiling heights and ceiling construction must be identified on the drawings.

- Drawings need to be clear, legible and understandable.  Drawings must be of a fire alarm design only.

CALCULATIONS

- Wire size, type, and resistance value

- Voltage drop calculations

- Battery calculations (minimum 60 hour battery back up)

SPECIFICATION SHEETS

All pertinent information shall be highlighted on the sheet.  Please provide cut sheets for all devices installed.

- FACP - Type, Listing, Current Draw

- Batteries – Type, Listing, Current Draw

- Smoke Detector – Type, Configuration, Spacing, Current Draw

- Heat Detector – Type, Configuration, Spacing, Current Draw

- Shunt Trip Heat Detector – Type, Rating, RTI-elevators

- Duct Detectors – Switch located on Fire Alarm panel (reset stations need to be located near the panel)

- Manual Pull Stations – Type, Configuration

- Audible Appliances – Type, Rating, Power Tap

- Alarm Temporal Pattern

- Visual Appliances – Type, Configuration

- Protective Covers – Type, Attenuation

- Water Flow Devices – Type, Configuration

- Supervisory Device – Type, Configuration

- Synchronization Module – Type, Current Draw

- Sequence of operation

- Class and Style of Signaling Line Circuits

- Class and Style of Notification Appliance Circuits

ADDITIONAL SUBMITTAL INFORMATION REQUIRED

- UL listed Remote station (Oak Lawn Central Dispatch)

- Graphic Map with initiating device locations

- Measured or ambient sound levels used

- Alarm signal devices shall produce a sound that exceeds the Average Ambient Sound Level Table (NFPA Standard 72)

- A Record of Completion – shall be prepared and submitted at final inspection (Record of completion can be found in Section 1-6.2 in NFPA 72)

- A stamped set of plans and cut sheets approved by the Fire District shall be available at the work-site at all times.

## ROUGH INSPECTION

A rough inspection of all fire alarm wiring shall be done by the Central Stickney Fire Protection District prior to the installation of drywall and/or ceiling materials.

## FINAL INSPECTION

No acceptance testing will be conducted prior to completion of construction.  A minimum of 2 working days is needed to schedule test.

Final acceptance is subject to Field Inspection.

An appointment is needed to be scheduled to have the final inspection completed. No testing will occur until all communicators are operational and being monitored.

The contractor must provide the Central Stickney Fire Protection District with a certificate stating that the fire protection systems are installed in full compliance with NFPA standards, IBC/IFC requirements, and that all acceptance tests have been conducted.  This certificate must be presented to the Fire Inspector at the time of the final acceptance test for the system.

The contractor must also supply a NFPA 72 worksheet at the time of the fire alarm acceptance test.

Appendix C is added to read as follows:

APPENDIX C

CENTRAL STICKNEY FIRE PROTECTION DISTRICT

SPRINKLER SYSTEM PLAN

SUBMITTAL CHECKLIST

This checklist is an effort to help provide a uniform approach for the design community and to provide owners and sprinkler system designers with complete sprinkler system design and submittal package requirements.

When submitting plans for review all plan submittals must include this Sprinkler System Plan Submittal Checklist or they will not be accepted.  By completing this checklist and including all of the necessary information requested it is the intent of this document to provide efficient and appropriate turnaround of the plans submitted.  It is the responsibility of the installer/designer to assure that all applicable code requirements are followed. (Check with the Village Code to find the current standards.)

The installation, renovation, addition, and/or maintenance of any sprinkler system shall comply with the following:

IMPORTANT:

No installation work shall be performed until the plans have been reviewed and approved.

Expect up to 10 working days for plan reviews per submittal

CHECKLIST: (All plans submitted must contain the following)

- Proof of Contractor’s license to be able to work within the city limits of unincorporated Stickney Township.

- Must be licensed to install Sprinkler Systems with the Illinois Office of the State Fire Marshal.

SPRINKLER SYSTEM DRAWINGS:

- Must submit Sprinkler System drawings to the Central Stickney Fire Protection District, Fire Prevention Bureau, 4951 S. Lotus Ave., Stickney Twp, IL 60638.  Any questions please contact the Bureau at 708-496-1268.

- Must submit 3 complete sets of sprinkler systems drawings and one on CD in PDF format and cut sheet/product information.  The scaled drawings must include the following:

      - Title block to include the following information: Property name and address, Sprinkler company name/Contractor name, address and phone number, date of drawing with space for revision dates, classification of the system per NFPA 13, who drew the drawing, and a detailed scope of work.

      - All hydraulic node points shall be shown clearly on the drawing.

      - The specific type and quantity of sprinklers shall be provided on every page.

      - All ceiling information including soffits, heights, construction type, slope, etc. shall be shown and noted with cross section detailed on the plans

      - Specific code sections and storage information shall be provided for all design densities over an Ordinary Group II

      - Provide a scaled site plan clearly showing the building fire department connection location and fire hydrant locations.

Drawings need to be clear, legible and understandable.  Drawings must be of a sprinkler system design only.

CALCULATIONS

- Hydraulic calculations shall clearly show the friction loss for the backflow preventer and include a graph curve sheet

- Fire hydrant flow test information shall be dated and less than one (1) year old.

SPECIFICATION SHEETS

All pertinent information shall be highlighted on the sheet.  Please provide cut sheets for all devices installed.

- All sprinklers, valves, etc shall be included on the cut sheets.

## ROUGH INSPECTION

A rough inspection of all sprinkler piping shall be done by the Central Stickney Fire Protection District prior to the installation of drywall and/or ceiling materials.

## TESTS

A flush of the underground water mains must be made prior to the connection to the sprinkler system.  All tests must be witnessed by the Central Stickney Fire Protection District.

All underground and overhead systems and piping should be hydrostatically tested with water at not less than 200 psi for two hours.  This test must be witnessed by the Central Stickney Fire Protection District.

When the system is complete a 2 inch main drain test must be completed and must be witnessed by the Central Stickney Fire Protection District.

When the system is completed a wet system inspectors test must be completed and the inspectors test report must be provided to the Central Stickney Fire Protection District.

## FINAL INSPECTION

No acceptance testing will be conducted prior to completion of construction.  A minimum of 2 working days is needed to schedule test.

Final acceptance is subject to Field Inspection.

An appointment is needed to be scheduled to have the final inspection completed.

The contractor must provide the Central Stickney Fire Protection District with a certificate stating that the fire protection systems are installed in full compliance with NFPA standards, IBC/IFC requirements, and that all acceptance tests have been conducted. This certificate must be presented to the Fire Inspector at the time of the final hydrostatic/acceptance test.

Appendix D is added to read as follows:

APPENDIX D

CENTRAL STICKNEY FIRE PROTECTION DISTRICT

WRITTEN REQUEST FOR RECORDS

Dear Chief (or designee):

(I), (We), are hereby requesting that (I), (We)

___________ Inspect the following records at the Central Stickney Fire Administration Office

___________ Receive copies of the following records from the Central Stickney Fire Protection 		           District

(Please be specific in listing records)			DATE AND LOCATION

Fire Report    Hazardous Spills    Car Fire    Other

All REQUESTS for ambulance reports must be accompanied by an ORIGINAL FORM SIGNED BY THE PATIENT.  Requests for fire reports must bear the original signature of the insured.

____________________			____________________________________

Date of Request				Print Name

____________________________________

Signature (s) of Requester (s)

____________________________________

Address

____________________________________

Phone #

(Office Use Only)

Date Request Received ________		______________________________

Signature

Attachment A is added to read as follows:

Attachment A

REFERENCED cODES AND STANDARDS:  The codes and standards referenced in this code shall be those that are listed in Chapter 45 and such codes and standards shall be considered part of the requirements of this code to the prescribed extent of each such reference.  Where differences occur between the provisions of this code and the referenced standards, the most stringent provision shall apply.

The following codes and editions listed are to be adopted in their entirety:

International Building Code 2009

NFPA 		10 		2010

13 		2010

13R		2010

13D		2010

14 		2010

15		2007

16		2007

20 		2010

24 		2010

25 		2008

70 		2008

72 		2010

96 		2008

- 2010

- 2006

Attachment B is added to read as follows:

## Attachment B FEES

Open Burning

## Resident					Commercial

1st Violation     – Warning			1st Violation    – Warning

2nd Violation    - $ 50.00			2nd Violation 	 -   $ 50.00 - $150.00

3rd Violation     - $100.00			3rd Violation    - $150.00 - $300.00

Fire watch:  A fee of $75.00 per hour for each Central Stickney Fire Protection District personnel assigned to the fire watch shall be charged. A minimum of 2 personal required.

Command Vehicle   $100.00 per hour

Engine                      $100.00 per hour

Truck                        $100.00 per hour

Specialized Equip.   $100.00 per hour

Emergency Access Maintenance:

It shall be the responsibility of every property owner and/or manager to provide current telephone numbers, current insurance information and contact persons to be notified in case of emergency involving their property and/or building.  Changes should be made in writing and sent or faxed to the Central Stickney Fire Protection District.

If a business changes locks, they must notify the Fire Department and get new keys for the Knox box.  If the Fire Department responds and the keys in the box are not valid the business may be fined.

Definitions:

False alarm is an alarm signal which indicated the existence of an emergency situation, when in fact no emergency exists, and shall include any alarm signal generated by any fire protection system by whatever means, but shall not include the following causes:

- Fire causing structural damage to the protected premises verified by the Fire District.

- Earthquakes causing structural damage to the protected premises.

- At the Fire Code officials discretion.

Vendor Meet: A meeting between the representatives from the Fire alarm Company, Fire District, Transmitting agency, Receiving Agency, and Building owner to resolve an ongoing alarm issue.  The Building Owner will be responsible for all fees incurred during the meeting.

Limited Service Alarms:  Any time an alarm is taken from a full service status due to a problem with alarm, alarm still able to send Fire Signals.

Out of Service Alarm:  Any alarm that is taken out of service due to some type of malfunction causing the alarm to not transmit signals properly.  Business placed on a 911 call in response only. Some businesses may require a Fire Watch.

False Alarm Fees:

The fees pertaining to False Alarms will be charged in accordance with the Central Stickney Fire Protection District Ordinance # 4-2009

# Out of Service Alarms:

The failure of any person to comply with the requirements contained in a written notice of a malfunction of equipment within three (3) days of receipt of such notice shall constitute an offense punishable by a fine of $100.00.  Such notice shall continue in force and effect until full compliance with the requirements stated therein and each and every failure to comply with such notice within 24 hours after the 3 days allowed for compliance constitute a separate offense.